## Rebate Areas
Instructions: Below fill in the Project and Contact Information completely. Next, mark an "X" for each potential rebate the project may be eligible for. Grayed out boxes indicate ineligible programs for participation. For each requested rebate, please either click the hyperlink to the right or visit the respective tab at the bottom of this spreadsheet. Once all the required documentation has been gathered, please contact Sustainable Building Coordinator for processing.
2022 Duke Energy Rebate Program
Project Information
Project # and Name
UF Building Name and Number
Project Square Feet
UF Project Manager
Contact Information
Item | Retrofit | New Construction | Incentive Requirements | Responsible Party
Duct Check and Repair Program |  | N/A | Duct Check and Repair Program | Facilities Services
Ceiling Insulation Upgrade |  | N/A | Ceiling Insulation Upgrade | Planning, Design & Construction
Wall Insulation Upgrade |  | N/A | Wall Insulation Upgrade | Planning, Design & Construction
High Efficiency Energy Recovery Ventilation (ERV) |  |  | Energy Recovery Ventilation | Planning, Design & Construction
Demand Control Ventilation |  |  | Demand Control Ventilation | Planning, Design & Construction
Small Heat Pumps (<65,000Btu/h) |  |  | Small Heat Pumps | Planning, Design & Construction
Large Heat Pumps (>65,000Btu/h) or Variable Refrigerant Flow (VRF) |  |  | Large Heat Pumps | Planning, Design & Construction
PTHPs & PTACs |  |  | PTHPs and PTACs | Planning, Design & Construction
Vertical Units Air Conditioners (VTAC) & Heat Pumps (>65,000 Btu/h) |  | N/A | Single Package Vertical Units | Planning, Design & Construction
Variable Refrigerant Flow |  |  | Variable Refrigerant Flow | Planning, Design & Construction
High Efficiency Chillers |  |  | High Efficiency Chillers | Planning, Design & Construction

## Duct
Duct Check and Repair Program |  |  |  |  | Updated: | 2022-01-31
Customer Qualifications |  |  | Required Documents for Submission Checklist
1 | Duct repairs must have both heating and cooling |  | 1 | Invoices from contractor indicating system and total material costs
2 | Duct repairs and sealing must be done by Duke Energy Florida Approved Contractors (link) |  | 2 | Contractor submit Duct Check form |  |  | Example
3 | Commercial multifamily units count on a per unit basis. (top floors |  | Duct Check Program
4 | Commercial multifamily units, if the contractor seals all joints and connections of the duct work, no duct test is required.
Rebate Home
| Rebate Calculation Estimator |  |  | Measure |  | Incentive
| Please identify the number of duct units tested |  |  | Duct Test (1st Unit) |  | 50
| Rebate from duct testing | 0 |  | Duct Test (for each additional unit) |  | 20 |  | Yes
| Do the duct units repaired have electrical heat installed in it? |  |  | Duct Repair non-ducted electrical heat (max) |  | 200 |  | No
| What is the repair costs for repairing ducts |  |  | Duct Repair ducted electrical heat (max) |  | 200 |  | Maybe
| Rebate from fixing duct work | 0 |  | Duct Sealing |  | 200
Are these ducts going to be sealed?
Rebate for sealing duct work
| Total Potential Rebates | #VALUE!
DAVID: DEF Rebates states that all maintenance measures have been eliminated…. Please confirm that this item still remains

## Ceiling
Ceiling Insulation Upgrade |  |  |  |  | Updated: | 2022-01-31
Customer Qualifications |  |  | Required Documents for Submission Checklist
1 | Building must be at least 2 years old |  | 1 | Invoices from contractor indicating system and total material costs
2 | Eligible facilities must have electric air conditioning and electric heating (non-portable) |  | 2 | Substantial Completion or Certificate of Occupancy form |  |  | Example
3 | Existing insulation must have an weighted average of less than or equal to R-12 |  | 3 | FINAL R-Value of Upgraded Insulation
4 | Must bring insulation to at least R-38 |  | 4 | Floor plan with Ceiling Area (SF) |  |  | Example
5 | Area must be at least 500sf |  | 5 | Contractors Submittal (specs/datasheets) |  |  | Example
Rebate Home |  |  | Ceiling Insulation
| Rebate Calculation Estimator |  |  |  | Measure | Incentive
| Please indicate the R-Value of the Ceiling insulation | R- |  |  | R-12 to R-38 | 0.17
| Please enter the total SF of celing area |  | SF
Total Potential Rebate

## Wall
Wall Insulation Upgrade | [5 empty] | Updated: | 2022-01-31
Customer Qualifications |  |  | Required Documents for Submission Checklist
1 | Building must be at least 2 years old |  | 1 | Invoices from contractor indicating system and total material costs
2 | Eligible facilities must have electric air conditioning and electric heating (non-portable) |  | 2 | Substantial Completion or Certificate of Occupancy form |  |  |  | Example
3 | Existing insulation must have an weighted average of less than or equal to R-16 |  | 3 | FINAL R-Value of Upgraded Insulation
4 | Must bring insulation to at least R-20 |  | 4 | Floor plan with Ceiling Area (SF) |  |  |  | Example
5 | Area must be at least 500sf |  | 5 | Contractors Submittal (specs/datasheets) |  |  |  | Example
Rebate Home |  |  | Wall Insulation
| Rebate Calculation Estimator |  |  |  | Measure | Incentive
| Please indicate the R-Value of the Wall insulation | R- |  |  | R-16 to R-20 | 0.1
| Please enter the total SF of wall area |  | SF
Total Potential Rebate

## ERV
High Efficiency Energy Recovery Ventilation (ERV) |  |  |  | Updated: | 2022-01-31
Customer Qualifications |  | Required Documents for Submission Checklist |  |  |  |  | yes
1 | Confirm ERV unit has an Air Conditioning, Heating, and Refrigeration Institute (AHRI) 1060 rating is greater than 65% winter/heating effectiveness (@ 100% air flow), **This is typically provided by the Engineer Of Record** | 1 | Invoices from contractor indicating system, ERV Quantities and total material costs |  |  |  | No
2 | ERV must have a minimum of 450 CFM per unit. | 2 | Contractor submittals with AHRI 1060 Rating (SCFM), Winter effectiveness (%) |  |  | Example
Rebate Home |  | 3 | Substantial Completion or Certificate of Operation form
High Efficiency Energy Recovery Ventilation
| Rebate Calculation Estimator |  | Measure | Incentive
| Please confirm that the ERV has the AHRI 1060 Winter Effectiveness rating over 65% |  | No electric heat | 0.75
| Please identify the size of the ERV measured in CFM |  | With electric heat | 0.75
Potential Rebate

## DCV
Demand Control Ventilation | [5 empty] | Updated: | 2022-01-31
Customer Qualifications |  |  | Required Documents for Submission Checklist
1 | HVAC equipment must be electric, and area where DCV is installed to be less than 500sf |  | 1 | Invoice memo from contractor indicating material costs of DCV |  |  |  | Example
2 | Provide an engineering report documenting the projected HVAC tonnage reduction. **Typically this is provided by the Engineer of Record** |  | 2 | Contractor's Submittal with system size (tons) and performance |  |  |  | Example
3 | The incentive rebate will not exceed 50% of the total HVAC project or service cost |  | 3 | Engineering report documenting DCV system and projected HVAC tonnage reduction. |  |  |  | Example
Rebate Home |  |  | 4 | Substantial Completion or Certificate of Operation form
Demand Control Ventilation
| Rebate Calculation Estimator |  |  | Measure | Incentive
| Please indicate the tonnage reduction identified in the engineered calculations | 0 |  | w/o electric heat | 50
| Potential Rebate | 0 |  | w/ electric heat | 50

## Small HP
Small Heat Pump (<65,000Btu/h or 5.5 tons) |  |  |  | Updated: | 2022-01-31
Customer Qualifications |  |  |  | Required Documents for Submission Checklist
* | Replacing Resistance Heat: Required cooling efficiency of 15 SEER and a minimum heating efficiency of 8.2 HSPF |  | 1 | Contractor invoice indicating system (make & model), total number of units and material costs
* | Replacing Heat Pump: Required cooling efficiency of 15 SEER and a minimum heating efficiency of 8.2 HSPF |  | 2 | Contractor submittals |  | Example
| NOTES |  | 3 | Substantial Completion or Certificate of Operation form
1 | If the capacity of the high-efficiency unit differs from that of the original unit - or if the high-efficiency unit is adding cooling to previously unconditined space - then cooling and heating load calculations must also be performed |  | Small Heat Pump
2 | Heat pump must be all electric
3 | All equipment must be new and not refurbished, previously installed, or used |  |  | SMALL HEAT PUMPS (≤ 65,000 Btu/h)
|  |  |  | Minimum Cooling Efficiency (SEER) | Minimum Heating Efficiency (HSPF) | Incentive per ton
Rebate Home |  |  |  | (SEER) | (HSPF) | (per ton)
|  |  |  | 15 | 8.2 | 50
| Rebate Calculation Estimator |  |  |  |  | Yes
| Please identify the total size (in tons) of the heat pump(s) that meet min performance |  |  |  |  | No
| Potential Rebate | 0

## Large HP
Large Heat Pumps (> 65,000 Btu/h or > 5.5 tons) | [5 empty] | Updated: | 2022-01-31
Customer Qualifications |  |  | Required Documents for Submission Checklist | [5 empty] | Unitary AC and Heat Pumps > 65,000 Btu/h |  |  |  | Variable Refrigerant Flow Multi-Split AC & Heat Pump
1 | Ensure all equipment meets Air Conditioning, Heating, and Refrigeration Institute (AHRI) certification efficeency data at Standard Rating Conditions AHRI 210/240-94 for units <135,000 Btu/h AHRI 340/360 for units > 135,000 Btu/h | 1 |  | Contractor invoice indicating system (make & model), total number of units and material costs |  |  |  |  | Equipment Type and Size Range | 2017 State Energy Code Standard |  | Minimum Efficiency Eligible for Incentive | Equipment Type and Size Range | Heating Type | Minimum Efficiency Eligible for Incentive
2 | Confirm that cooling and heating load calculation are performed if the capacity of the high efficiency unit differs from that of the original unit or if the high efficiency unit is adding cooling or heating to previously unconditioned space. | 2 |  | Contractor submittals |  |  |  | Example | Air- Cooled | Air Conditioner | Heat Pump | (Efficiencies exceed code by at least 10%) | VRF Multi-Split (Air Cooled)
3 | Single Package Vertical Units also qualify for this rebate | 3 |  | Substantial Completion or Certificate of Operation form |  |  |  |  | 65,000-135,000 Btu/h (5.5 - 11.25 tons) | 11.2 EER | 11.0 EER 3.3 COP | 12.1 EER or 3.63 COP | <65,000Btu/h (<5.5 tons) | All | 14.3 SEER
Rebate Home |  | Unitary AC Units & Heat Pumps (>65,000) | [6 empty] | 135,001 – 240,000 Btu/h (11.25 - 20 tons) | 11.0 EER | 10.6 EER 3.2 COP | 11.69 EER or 3.52 COP | 65,000-135,000 Btu/h (5.5 - 11.25 tons) | No heating or Electric Resistance All other types | 12.3 EER 12.1 EER
[9 empty] | 240,001 – 760,000 Btu/h (20 - 63.3 tons) | 10.0 EER | 9.5 EER 3.2 COP | 10.63 EER of 3.27 COP | 135,001 – 240,000 Btu/h (11.25 - 20 tons) | No heating or Electric Resistance All other types | 12.3 EER 11.8 EER
| Rebate Calculation Estimator |  | Measure |  |  | Incentive | Unit |  | >760,000 Btu/h (63.3 tons) | 9.7 EER | 9.5 EER 3.2 COP | 10.31 EER of 3.52 COP | 240,001 – 760,000 Btu/h (20 - 63.3 tons) | No heating or Electric Resistance All other types | 11.0 EER 10.7 EER
| Please identify the number of AHU units associated to the project |  | Large AC Units and Heat Pumps |  |  | 50 | Per ton |  | Water-Cooled | Air Conditioner | Heat Pump |  | VRF Multi-Split Heat Pump
[9 empty] | 65,000-135,000 Btu/h (5.5 - 11.25 tons) | 12.1 EER | N/A | 13.3 EER | <65,000Btu/h (<5.5 tons) | All | 14.3 SEER 8.4 HSPF
[9 empty] | 135,000 - 240,000 Btu/h (11.25 - 20 tons) | 12.5 EER | N/A | 13.7 EER | 65,000-135,000 Btu/h (5.5 - 11.25 tons) | No heating or Electric Resistance All other types | 12.0 EER/3.6 COP 11.8 EER/3.6 COP
[9 empty] | 240,000 - 760,000 Btu/h (20 - 63.3 tons) | 12.4 EER | N/A | 13.6 EER | 135,001 – 240,000 Btu/h (11.25 - 20 tons) | No heating or Electric Resistance All other types | 11.6 EER/3.6 COP 11.4 EER/3.5 COP
[9 empty] | over 760,000 Btu/h (over 63.3 tons) | 12.2 EER | N/A | 13.4 EER | 240,001 – 760,000 Btu/h (20 - 63.3 tons) | No heating or Electric Resistance All other types | 10.4 EER/3.5 COP 10.2 EER/3.5 COP
=IF(OR($D$11=4,$D$11>4),D12,"")
MBH
MBTU/H
BTU/H
Tons
[5 empty] | Total Potential Rebate | 0

## PTAC
Packaged Terminal Heat Pumps (PTHPs) & Packaged Terminal Air Conditioners (PTACs) |  |  |  | Updated: | 2022-01-31
Customer Qualifications |  | Required Documents for Submission Checklist |  |  |  | PACKAGED TERMINAL AIR CONDITONERS (PTACs) (AHRI 310/380 Test Standards) |  |  | New Construction | PACKAGED TERMINAL HEAT PUMPS (PTHPs) Replacing PTACs (AHRI 310/380 Test Standards) |  |  | PACKAGED TERMINAL HEAT PUMPS (PTHPs) Replacing PTACs (AHRI 310/380 Test Standards)
1 | Provide an itemized inventory of equipment installed and Air Conditioning, Heating, and Refrigeration Institute (AHRI) certification data at Standard Rating Conditions (AHRI 310/380) | 1 | Contractor invoice indicating system (make & model), total number of units and material costs |  |  | Cooling Capacity (Btu/h) | Cooling Efficiency (EER) |  | Retrofit | Cooling Capacity (Btu/h) | Cooling Efficiency (EER) |  | Cooling Capacity (Btu/h) | Heating Efficiency (COP)
2 | Cooling load calculations msut be performed if the capacity of the high efficiency unit differs from that of the original unit or if the high efficiency unit is adding cooling to previously unconditioned space. | 2 | Contractor's submittal |  |  |  | Minimum Efficiency Eligible for Incentive (Must be 25% more efficient than Current Fl Energy Code) |  |  |  | Minimum Efficiency Eligible for Incentive (Must be 25% more efficient than Current Fl Energy Code) |  |  | Minimum Efficiency Eligible for Incentive (Must be 25% more efficient than Current Fl Energy Code)
| Rebate Home | 3 | Substantial Completion or Certificate of Operation form |  |  |  | New Construction | Retrofit | PTAC |  | New Construction | Retrofit |  | New Construction | Retrofit
|  | PTHPs and PTACs |  |  |  | All Capacities | Formula for minimum Efficiency for an Incentive (14-(0.3 x Cap/1000)) x 1.25 Example - 8,000 Btu Unit (14-(0.3x8)) x1.25 (14-2.4) x1.25 11.6 x 1.25 14.5 EER | Formula for minimum Efficiency for an Incentive (10.9 - (0.213 x Cap/1000)) x 1.25 Example - 8,000 Btu Unit (10.9 - (0.213x8)) x1.25 (10.9 – 1.7) x 1.25 9.19 x 1.25 11.49 EER | PTHP | All Capacities | Formula for minimum Efficiency for an Incentive (14- (0.3 x Cap/1000)) x 1.25 EER Example - 8,000 Btu Unit (14 - (0.3 x 8)) x 1.25 (14 - 2.4) x 1.25 11.6 x 1.25 14.5 EER | Formula for minimum Efficiency for an Incentive (10.8 - (0.213 x Cap/1000)) x 1.25 EER Example - 8,000 Btu Unit (10.8 - (0.213 x 8)) x 1.25 (10.8 – 1.7) x 1.25 9.1 x 1.25 11.37 EER | All Capacities | Formula for minimum Efficiency for an Incentive (3.2- (0.026 x Cap/1000)) x 1.25 COP Example - 8,000 Btu Unit (3.2- (0.026 x 8)) x 1.25 (3.2 - .2) x 1.25 3. x 1.25 3.75 COP | Formula for minimum Efficiency for an Incentive (2.9 - (0.026 x Cap/1000)) x 1.25 COP Example - 8,000 Btu Unit (2.9 - (0.026 x 8)) x 1.25 (2.9 - .2) x 1.25 3.1 x 1.25 3.87 COP
[10 empty] | *No rebates are available for replacing PTHP’s |  |  | *No rebates are available for replacing PTHP’s
| Rebate Calculation Estimator |  |  |  |  | Measure |  | Incentive | Yes
| Please indicate if this project is either New Construction or Retrofit |  |  |  |  | PTACs replacing less efficent PTAC (per ton) |  | 67 | No
| Is the project using Packaged Terminal Air Conditioners (PTACs) or Packaged Terminal Heat Pumps (PTHPs)? |  |  |  |  | PTHP replacing PTACs (per ton) |  | 67
Please indicate the total number of units (max 5)
| Potential Rebate |  | 0

## VTAC
Vertical Terminal Air Conditioner and Heat Pump |  |  |  | Updated: | 2022-01-31
Customer Qualifications |  | Required Documents for Submission Checklist | [5 empty] | Single–Package Vertical Straight Cool and Heat Pump (ASHRAE Standard 90.1-2004)
1 | All equipment installations shall exceed the minimum efficiency requirements set by federal, state, and local code by 10%. | 1 | Contractor invoice indicating system (make & model), total number of units and material costs |  |  |  | Yes |  | Heating Efficiency (COP) | Cooling Efficiency (EER)
2 | Heat pump must be all electric | 2 | Contractor submittals |  |  | Exanple | No | Cooling Capacity | Minimum Efficiency Eligible for Incentive | Minimum Efficiency Eligible for Incentive
3 | All equipment must be new and not refurbished, previously installed, or used | 3 | Substantial Completion or Certificate of Operation form |  |  |  |  | < 65,000 Btu/h < 5.5 Tons | 3.3 | 9.9
Rebate Home |  | Vertical Terminal Air Conditioner and Heat Pump | [5 empty] | 65,000 - 135,000 Btu/h 5.5 - 11.25 Tons | 3.2 | 9.7
[8 empty] | 135,000 - 240,000 Btu/h 11.25 - 20 Tons | 3.1 | 9.4
| Rebate Calculation Estimator |  | Measure |  | Incentive | Unit |  | "For straight cooled equipment just EER only as COP is not required"
| Does the VTAC meet or exceed the heating/cooling requirements found in the table to the right? |  | Replacing heat pump |  | 50 | per ton
| Do these heat pumps have heat resistance? |  | Replacing resistance heat |  | 50 | per ton
What is the size of the units being replaced (in tons)?

## VRF
Variable Refrigerant Flow (Air Conditioning and Heat Pumps) |  |  |  |  | Updated: | 2022-01-31
| Customer Requirements |  |  | Required Documents for Submission Checklist |  |  |  | Variable Refrigerant Flow Multi-Split Air Conditioners and Heat Pumps
1 | All equipment installations shall exceed the minimum efficiency requirements set by federal, state, and local code by 10% |  | 1 | Contractor invoice indicating system (make & model), total number of units and material costs |  |  |  | Equipment Type | Cooling Capacity | Heating Type | Minimum Efficiency Eligible for Incentive | Yes
| Rebate Home |  | 2 | Contractors submittal |  |  | Example | VFR Multi-Split AC’s (Air Cooled) | < 65,000 (Btu/h) 5.5 (tons) | All | 14.3 SEER | No
|  |  | 3 | Substantial Completion or Certificate of Operation form |  |  | Example |  | > 65,000 - 135,000 (Btu/h) 5.5 - 11.25 (tons) | No Heating – or has Electric resistance heating | 12.3 EER
|  |  | Variable Refrigerant Flow | [6 empty] | All other types of heating | 12.1 EER
[9 empty] | 135,000 - 240,000 (Btu/h) 11.25 - 20 (tons) | No Heating – or has Electric resistance heating | 12.1 EER
| Rebate Calculation Estimator |  |  | Measure |  | Incentive | Unit |  |  | All other types of heating | 11.8 EER
| Does the VRF system meet the minimumim efficiencies shown in the chart to the right? | Yes |  | Variable |  | 50 | Per ton |  | 240,000 - 760,000 (Btu/h) 20 - 63.3 (tons) | No Heating – or has Electric resistance heating | 11.0 EER
| Please identify the total cooling capacity of the VRF being installed (in tons) | 10 | [7 empty] | All other types of heating | 10.7 EER
| Total Potential Rebate | 500 | [5 empty] | VFR Multi-Split Heat Pumps (Air Cooled) | < 65,000 (Btu/h) 5.5 (tons) | All | 14.3 SEER 8.4 HSPF
[9 empty] | > 65,000 - 135,000 (Btu/h) 5.5 - 11.25 (tons) | No Heating – or has Electric resistance heating | 12 EER 3.6 COP
[10 empty] | All other types of heating | 11.8 EER 3.6 COP
[9 empty] | 135,000 - 240,000 (Btu/h) 11.25 - 20 (tons) | No Heating – or has Electric resistance heating | 11.6 EER 3.6 COP
[10 empty] | All other types of heating | 11.4 EER 3.5 COP
[9 empty] | 240,000 - 760,000 (Btu/h) 20 - 63.3 (tons) | No Heating – or has Electric resistance heating | 10.4 EER 3.5 COP
[10 empty] | All other types of heating | 10.2 EER 3.5 COP
NOTE: Water-cooled EER is at Standard Rating of 85° F entering water

## Chillers
High Efficiency Chillers |  |  |  |  | Updated: | 2022-01-31
| Customer Requirements |  |  | Required Documents for Submission Checklist |  |  |  | EEB Incentive Eligibility Requirements
1 | Chiller efficiencies and performance specifications should be calculated at Air Conditioning, Heating, and Refrigeration Institute (AHRI) test conditions (550/590 Test Standards.) |  | 1 | Contractor invoice indicating system (make & model), total number of units and material costs |  |  |  | AIR COOLED AND WATER COOLED ELECTRIC CHILLERS (AHRI 550/590 Test Standards)
2 | For air cooled and water cooled electric chillers, confirm that cooling load calculations are performed if the capacity of the high efficiency unit differs from that of the original unit or if the high efficiency uint is adding cooling to previously unconditioned space. |  | 2 | Contractors submittal |  |  | Example | Chiller Type and Size Range | Full Load vs Part Load | 2017 State Energy Code Standard | Minimum Efficiency Eligible for Incentive
3 | Minimum efficiency can beat either Full Load (FL)or Integrated Part Load Value (IPLV). |  | 3 | Substantial Completion or Certificate of Operation form |  |  | Example | Water Cooled Operated Centrifugal
| Rebate Home |  | High Efficiency Chillers |  |  |  |  | Under 150 tons | Full Load: Integrated Part Load: | 0.61 kW/ton 0.55 kW/ton | 0.54 kW/ton 0.49 kW/ton
[8 empty] | 150-300 tons | Full Load: Integrated Part Load: | 0.61 kW/ton 0.55 kW/ton | 0.54 kW/ton 0.49 kW/ton
| Rebate Calculation Estimator |  |  | Measure |  | Incentive | Unit | 300-400 tons | Full Load: Integrated Part Load: | 0.56 kW/ton 0.52 kW/ton | 0.50 kW/ton 0.46 kW/ton
| Please identify the total cooling capacity of the chiller being installed (in tons) |  |  | Air and Water cooled |  | 20 | Per ton | 400-600 tons | Full Load: Integrated Part Load: | 0.56 kW/ton 0.50 kW/ton | 0.50 kW/ton 0.45 kW/ton
| Total Potential Rebate | 0 | [5 empty] | Over 600 tons | Full Load: Integrated Part Load: | 0.56 kW/ton 0.50 kW/ton | 0.50 kW/ton 0.45 kW/ton
Water Cooled Positive Displacement
[8 empty] | Under 75 tons | Full Load: Integrated Part Load: | 0.75 kW/ton 0.60 kW/ton | 0.67 kW/ton 0.54 kW/ton
[8 empty] | 75-150 tons | Full Load: Integrated Part Load: | 0.72 kW/ton 0.56 kW/ton | 0.64 kW/ton 0.504 kW/ton
[8 empty] | 150-300 tons | Full Load: Integrated Part Load: | 0.66 kW/ton 0.54 kW/ton | 0.59 kW/ton 0.48 kW/ton
[8 empty] | 300-600 tons | Full Load: Integrated Part Load: | 0.61 kW/ton 0.52 kW/ton | 0.54 kW/ton 0.46 kW/ton
[8 empty] | Over 600 tons | Full Load: Integrated Part Load: | 0.56 kW/ton 0.50 kW/ton | 0.50 kW/ton 0.45 kW/ton
Air Cooled
[8 empty] | Under 150 tons | Full Load: Integrated Part Load: | 10.10 EER 13.70 EER | 11.11 EER (Btu/W) 15.07 EER (Btu/W)
[8 empty] | Greater 150 tons | Full Load: Integrated Part Load: | 10.10 EER 14.00 EER | 11.11 EER (Btu/W) 15.4 EER (Btu/W)
*NPLV can be used if IPLV is not available. Must be better than IPLV value